## Sheet1
Compute Pounds of Water per cubic Foot of Air based on Relative Humidity & Temperature
Temp F | 40
Temp in C | 4.4444
Relative Humidity | 99.999
Building Size
Grams per Cubic Meter | 6.5504 |  | Length Foot | 52
Pounds per Cubic Meter | 0.014431 |  | Width foot | 36
Cubic Foot Per Meter | 35.3147 |  | Height foot | 12
Pounds Per Cubic Foot | 0.00040863 |  | Cubic Foot | 22464
kg per Cubic Meter | 0.0065504 |  | Cubic Meter | 636.109
Ounces per Cubic Foot | 0.23089 |  | Grams Water in Air | 4166.7379
|  |  | Pounds of Water in Air | 9.1861
|  |  | Gallons of Water in Air | 1.1007
Online Calculator for kg per Cubic Meter
Process Heating Chart
Calculate Amount of Water Lost between 2 temp with a given Dessicant
Molecular Siev hold a pretty consistent 15% of weight across a wide range of humidity
while calcium chloride varies considerably across humidity
|  |  | Target Number of Regeneration cycles | 6
|  | 1001.154 | Absorption as Function of weight | 15%
|  |  | Desicant required to Store fraction of water | 61.2406
|  |  | Desicant adjusted for number of cycles per day | 10.2068
|  |  | Estimated Change as Portion of total | 40%
|  |  | Adjusted pounds of Desicant needed | 25.5169
|  |  | max pounds water contained in Desicant | 3.8275
Drying Required to Prevent Condensation
|  |  | Dewpoint of 80% RH @ 60F | 12.12 | 0.44554
How much do we need to dry the air to ensure Dewpoint is not reached
for the interior air? To know this we need to know the probable lowest
Temperature we are likely to encounter.
for example: If low temp will be 40F or 4.4C the air can hold 6.6 grams at 100% vs our 12 grams.
In essence we will need to remove 5.4 grams or 44% of the water.
If the prior night was similar and the structure has minimal leaks then
it may already be at the lower humidity from the night befor and only
require a little drying. The more leaky the structure the more drying will be required.
Drying By Mixing
If we take 80* RH air and dry it to 10% then allow them to mix then
how many cubic foot of do we need to mix reduce overall humidty to 45%
|  |  | Grams per M3 80% @ 60F | 10.606
|  |  | Grams per M3 10% @ 60F | 1.326
|  |  | Grams per M3 45% @ 60F | 5.966
|  |  |  | Result Grams @ mixing Ratio | Mix Ratio Parts@Dry to parts@Moist
|  |  | Resulting Grams per M3 @ Mixing Ratio | 8.4645 | 0.3
|  |  | Resulting Grams per M3 @ Mixing Ratio | 7.5127 | 0.5
|  |  | Resulting Grams per M3 @ Mixing Ratio | 6.7848 | 0.7
|  |  | Resulting Grams per M3 @ Mixing Ratio | 5.966 | 1
|  |  | Resulting Grams per M3 @ Mixing Ratio | 4.4193 | 2
|  |  | Resulting Grams per M3 @ Mixing Ratio | 3.646 | 3
|  |  | Resulting Grams per M3 @ Mixing Ratio | 3.182 | 4
|  |  | Resulting Grams per M3 @ Mixing Ratio | 2.8727 | 5
|  |  | Resulting Grams per M3 @ Mixing Ratio | 2.6517 | 6
|  |  | Resulting Grams per M3 @ Mixing Ratio | 2.486 | 7
|  |  | Resulting Grams per M3 @ Mixing Ratio | 2.3571 | 8
|  |  | Resulting Grams per M3 @ Mixing Ratio | 2.254 | 9
|  |  | Resulting Grams per M3 @ Mixing Ratio | 2.1696 | 10
|  |  | Resulting Grams per M3 @ Mixing Ratio | 2.0993 | 11
|  |  | Resulting Grams per M3 @ Mixing Ratio | 2.0398 | 12
|  |  | Resulting Grams per M3 @ Mixing Ratio | 1.9889 | 13
|  |  | Resulting Grams per M3 @ Mixing Ratio | 1.9447 | 14
|  |  | Resulting Grams per M3 @ Mixing Ratio | 1.906 | 15
|  |  | Resulting Grams per M3 @ Mixing Ratio | 1.8719 | 16